## Sheet1
module | reg_type | reg_address | reg_bit_flag | reg_value | min_value | max_value | error_value | default_value | resolution | simulation
TEMPERATURE_SENSING1 | HR | 0 | 16 | 44 | -50 | 500 | 1 | 99 | 0.1 | TRUE
TEMPERATURE_SENSING2 | HR | 1 | 16 | 55 | -50 | 500 | 1 | 99 | 0.1 | TRUE
TEMPERATURE_SENSING3 | HR | 2 | 16 | 34 | -50 | 500 | 1 | 99 | 0.1 | TRUE
TEMPERATURE_SENSING4 | HR | 3 | 16 | 33 | -50 | 500 | 1 | 99 | 0.1 | TRUE
CURRENT_SENSING1 | HR | 4 | 16 | 33 | 0 | 200 | 1 | 70 | 0.1 | TRUE
CURRENT_SENSING2 | HR | 5 | 16 | 33 | 0 | 200 | 1 | 70 | 0.1 | TRUE
CURRENT_SENSING3 | HR | 6 | 16 | 33 | 0 | 200 | 1 | 70 | 0.1 | TRUE
POWER_SENSING | HR | 7 | 16 | 33 | 0 | 200 | 1 | 240 | 1 | TRUE
TACO_MONITOR1 | HR | 8 | 16 | 33 | 0 | 500 | 1 | 300 | 1 | TRUE
TACO_MONITOR2 | HR | 9 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
TACO_MONITOR3 | HR | 10 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
TACO_MONITOR4 | HR | 11 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
TACO_MONITOR5 | HR | 12 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
TACO_MONITOR6 | HR | 13 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
TACO_MONITOR7 | HR | 14 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
TACO_MONITOR8 | HR | 15 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
TACO_MONITOR9 | HR | 16 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
TACO_MONITOR10 | HR | 17 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
TACO_MONITOR11 | HR | 18 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
TACO_MONITOR12 | HR | 19 | 16 | 33 | 0 | 1000 | 1 | 300 | 1 | TRUE
FAULT_MONITOR1 | HR | 20 | 0 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
FAULT_MONITOR2 | HR | 20 | 1 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
FAULT_MONITOR3 | HR | 20 | 2 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT1 | HR | 20 | 3 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT2 | HR | 20 | 4 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT3 | HR | 20 | 5 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT4 | HR | 20 | 6 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT5 | HR | 20 | 7 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT6 | HR | 20 | 8 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT7 | HR | 20 | 9 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT8 | HR | 20 | 10 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT9 | HR | 20 | 11 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT10 | HR | 20 | 12 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT11 | HR | 20 | 13 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TACO_MONITOR_FAULT12 | HR | 20 | 14 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
VOLTAGE_HIGH | HR | 21 | 0 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
VOLTAGE_LOW | HR | 21 | 1 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
G1_CURRENT_HIGH | HR | 21 | 2 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
G2_CURRENT_HIGH | HR | 21 | 3 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
G3_CURRENT_HIGH | HR | 21 | 4 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TEMPERATURE_ZONE1_HIGH | HR | 21 | 5 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TEMPERATURE_ZONE2_HIGH | HR | 21 | 6 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TEMPERATURE_ZONE3_HIGH | HR | 21 | 7 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE
TEMPERATURE_ZONE4_HIGH | HR | 21 | 8 | 33 | 0 | 1 | 1 | 1 | 1 | TRUE

## Sheet3
S No | Components | adress_count | Data byte | Bytes | Resolution | Range | Modbus Register
1 | Temperature 1 | 1 | 16 bit signed | 2 | 0.1C | -70°C to +500°C | 40000
2 | Temperature 2 | 1 | 16 bit signed | 2 | 0.1C | -70°C to +500°C | 40001
3 | Temperature 2 | 1 | 16 bit signed | 2 | 0.1C | -70°C to +500°C | 40002
4 | Temperature 2 | 1 | 16 bit signed | 2 | 0.1C | -70°C to +500°C | 40003
5 | Group1 Fan's Current | 1 | 16 bit signed | 2 | 0.1mA | 0 to 3.3A | 40004
6 | Group2 Fan's Current | 1 | 16 bit signed | 2 | 0.1mA | 0 to 3.3A | 40005
7 | Group3 Fan's Current | 1 | 16 bit signed | 2 | 0.1mA | 0 to 3.3A | 40006
8 | Voltage | 1 | 16 bit signed | 2 | 0.1V | 0 to 600V | 40007
9 | Fan1 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40008
10 | Fan2 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40009
11 | Fan3 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40010
12 | Fan4 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40011
13 | Fan5 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40012
14 | Fan6 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40013
15 | Fan7 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40014
16 | Fan8 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40015
17 | Fan9 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40016
18 | Fan10 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40017
19 | Fan11 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40018
20 | Fan12 Frequency | 1 | 16 bit signed | 2 | 1hz | 30Hz to 500Hz | 40019
21 | Taco monitors and Fault monitor Bit0:Fan1 RPM fault Bit1:Fan2 RPM fault Bit2:Fan3 RPM fault Bit3:Fan4 RPM fault Bit4:Fan5 RPM fault Bit5:Fan6 RPM fault Bit6:Fan7 RPM fault Bit7:Fan8 RPM fault Bit8:Fan9 RPM fault Bit9:Fan10 RPM fault Bit10:Fan11 RPM fault Bit11:Fan12 RPM fault Bit12: Group1 Alert Bit13: Group2 Alert Bit14: Group3 Alert" | 1 | 16 bit signed | 2 |  | 0 to 1 | 40020
21 | Fan Voltage/Current/Temp Alerts Bit0:24V High Bit1:24V High Bit2: G1 Fans current High Bit3: G2 Fans current High Bit4: G3 Fans current High Bit5:Temperature Zone1 High Bit6: Temperature Zone2 High Bit7: Temperature Zone3 High Bit8: Temperature Zone4 High | 1 | 16 bit signed | 2 |  | 0 to 1 | 40021

## Sheet2
sensor_name | row_count | address_count | update_duration_msec | element_type | simulation | address | block_name | Data_Type | Data_format | Default_Data | 1_Point_Calibration_Value | 2_Point_Calibration_Value | Data_Range_Min | Data_Range_Max | Alarm_LL_Min | Alarm_LL_Max | Alarm_L_Min | Alarm_L_Max | Alarm_H_Min | Alarm_H_Max | Alarm_HH_Min | Alarm_HH_Max
PH_PROBE | 4 | 2 | 1000 | INPUT_REGISTERS | YES | 0 | PH_PROBE_VALUE | float | decimal |  |  |  | 7.4 | 7.6 | 5 | 5 | 5.1 | 6 | 9 | 9.1 | 10 | 10.1
|  | 1 |  | DISCRETE_INPUTS | NO | 30 | PH_PROBE_ERROR | int | decimal | 0
|  | 2 |  | INPUT_REGISTERS | NO | 48 | PH_CALIBRATION_SLOPE | float | decimal | 1 | 1.01 | 1.02
|  | 2 |  | INPUT_REGISTERS | NO | 50 | PH_CALIBRATION_INTERCEPT | float | decimal | 0 | 0.02 | 0.03
ORP | 4 | 2 | 1000 | INPUT_REGISTERS | YES | 2 | ORP_VALUE | float | decimal |  |  |  | 450 | 450 | 250 | 250 | 300 | 300 | 600 | 650 | 700 | 750
|  | 1 |  | DISCRETE_INPUTS | NO | 29 | ORP_ERROR | int | decimal | 0
|  | 2 |  | INPUT_REGISTERS | NO | 44 | ORP_CALIBRATION_SLOPE | float | decimal | 1 | 1.01 | 1.02
|  | 2 |  | INPUT_REGISTERS | NO | 46 | ORP_CALIBRATION_INTERCEPT | float | decimal | 0 | 0.03 | 0.02
CORROSION_PROBE_1 | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 4 | CORROSION_PROBE_1_VALUE | float | decimal |  |  |  | 0.2 | 3.9 | 0.05 | 0.05 | 0.1 | 0.1 | 4 | 4 | 4.5 | 4.5
|  | 1 |  | DISCRETE_INPUTS | NO | 49 | CORROSION_PROBE_1_NOT_CONNECTED | int | decimal | 0
CORROSION_PROBE_2 | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 6 | CORROSION_PROBE_2_VALUE | float | decimal |  |  |  | 0.4 | 0.4 | 0.01 | 0.01 | 0.02 | 0.02 | 0.5 | 0.65 | 0.8 | 0.8
|  | 1 |  | DISCRETE_INPUTS | NO | 58 | CORROSION_PROBE_2_NOT_CONNECTED | int | decimal | 0
RTD | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 8 | RTD | float | decimal |  |  |  | 4.45 | 4.45 | 4.43 | 4.43 | 15.56 | 15.56 | 32.22 | 32.22 | 48.89 | 48.89
|  | 1 | 1000 | DISCRETE_INPUTS | NO | 48 | CORROSION_PROBE_1_RTD_ERROR | int | decimal | 0
RTD_CORROSION | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 10 | RTD_CORROSION | float | decimal |  |  |  | 4.45 | 4.45 | 4.43 | 4.43 | 15.56 | 15.56 | 32.22 | 32.22 | 48.89 | 48.89
|  | 1 | 1000 | DISCRETE_INPUTS | NO | 57 | CORROSION_PROBE_2_RTD_ERROR | int | decimal | 0
RTD_TOROIDAL | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 12 | RTD_TOROIDAL | float | decimal |  |  |  | 4.45 | 4.45 | 4.43 | 4.43 | 15.56 | 15.56 | 32.22 | 32.22 | 48.89 | 48.89
|  | 1 |  | DISCRETE_INPUTS | NO | 23 | TOROIDAL_RTD_ERROR | int | decimal | 0
ANALOG_IN_1 | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 14 | ANALOG_IN_1_VALUE | float | decimal |  |  |  | 12 | 12.1 | 4.9 | 4.9 | 10 | 10 | 400 | 450 | 500 | 500.1
|  | 1 |  | DISCRETE_INPUTS | NO | 18 | ANALOG_IN_1_ERROR | int | decimal | 0
ANALOG_IN_2 | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 16 | ANALOG_IN_2_VALUE | float | decimal |  |  |  | 12 | 12.1 | 10 | 10 | 10.1 | 15 | 300 | 399.9 | 400 | 400.1
|  | 1 |  | DISCRETE_INPUTS | NO | 19 | ANALOG_IN_2_ERROR | int | decimal | 0
ANALOG_IN_3 | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 18 | ANALOG_INPUT_3_VALUE | float | decimal |  |  |  | 7 | 7.5 | 5 | 5 | 6 | 6 | 9.5 | 9.5 | 10 | 10.1
|  | 1 |  | DISCRETE_INPUTS | NO | 20 | ANALOG_INPUT_3_ERROR | int | decimal | 0
ANALOG_IN_4 | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 20 | ANALOG_INPUT_4_VALUE | float | decimal |  |  |  | 7 | 7.5 | 5 | 5 | 6 | 6 | 9.5 | 9.5 | 10 | 10.1
|  | 1 |  | DISCRETE_INPUTS | NO | 21 | ANALOG_INPUT_4_ERROR | int | decimal | 0
ANALOG_OUTPUT_1 | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 22 | DAC_1_VALUE | float | decimal |  |  |  | 100 | 200 | 400 | 500 | 0 | 1 | 3 | 20 | 20 | 30
|  | 1 |  | DISCRETE_INPUTS | NO | 16 | DAC_1_ERROR | int | decimal | 0
ANALOG_OUTPUT_2 | 2 | 2 | 1000 | INPUT_REGISTERS | YES | 24 | DAC_2_VALUE | float | decimal |  |  |  | 100 | 200 | 400 | 500 | 0 | 1 | 3 | 20 | 20 | 30
|  | 1 |  | DISCRETE_INPUTS | NO | 17 | DAC_2_ERROR | int | decimal | 0
ELECTRODE_CONDUCTIVITY | 4 | 2 | 1000 | INPUT_REGISTERS | YES | 26 | ELECTRODE_CONDUCTIVITY_VALUE | float | decimal |  |  |  | 999.9 | 1000.1 | 600 | 600 | 700 | 700 | 1500 | 1501 | 1600 | 1601
|  | 1 |  | DISCRETE_INPUTS | NO | 28 | ELECTRODE_CONDUCTIVITY_ERROR | int | decimal | 0
|  | 2 |  | INPUT_REGISTERS | NO | 40 | ELECTRODE_CONDUCTIVITY_CALIBRATION_SLOPE | float | decimal | 1 | 1.02 | 1.01
|  | 2 |  | INPUT_REGISTERS | NO | 42 | ELECTRODE_CONDUCTIVITY_CALIBRATION_INTERCEPT | float | decimal | 0 | 0.02 | 0.01
TOROIDAL_CONDUCTIVITY | 4 | 2 | 1000 | INPUT_REGISTERS | YES | 28 | TOROIDAL_CONDUCTIVITY_VALUE | float | decimal |  |  |  | 200.1 | 1999.9 | 100 | 100 | 100.1 | 200 | 2000 | 2499.9 | 2500 | 2500.1
|  | 1 |  | DISCRETE_INPUTS | NO | 22 | TOROIDAL_CONDUCTIVITY_ERROR | int | decimal | 0
|  | 2 |  | INPUT_REGISTERS | NO | 36 | TOROIDAL_INPUT_CALIBRATION_SLOPE | float | decimal | 1 | 1.03 | 1.04
|  | 2 |  | INPUT_REGISTERS | NO | 38 | TOROIDAL_INPUT_CALIBRATION_INTERCEPT | float | decimal | 0 | 0.02 | 0.01
INTERLOCK | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 0 | INTERLOCK_VALUE | int | decimal | 0
FLOW_SWITCH | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 1 | FLOW_SWITCH_VALUE | int | decimal | 0
SB_BAUD_RATE_DIP_SWITCH | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 8 | BAUD_RATE_DIP_SWITCH_VALUE | int | decimal | 0
SB_MODBUS_ID_DIP_SWITCHES | 1 | 4 | 1000 | DISCRETE_INPUTS | NO | 9 | MODBUS_ID_DIP_SWITCHS_VALUE | int | decimal | 0,0,0,1
MODE_STATUS | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 15 | MODE_STATUS | int | decimal | 1
DIGITAL_INPUT_1_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 24 | DIGITAL_INPUT_1_ERROR | int | decimal | 0
DIGITAL_INPUT_2_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 25 | DIGITAL_INPUT_2_ERROR | int | decimal | 0
DIGITAL_INPUT_3_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 26 | DIGITAL_INPUT_3_ERROR | int | decimal | 0
DIGITAL_INPUT_4_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 27 | DIGITAL_INPUT_4_ERROR | int | decimal | 0
SENSOR_EEPROM_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 31 | SENSOR_EEPROM_ERROR | int | decimal | 0
UART_TO_UART_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 63 | UART_TO_UART_ERROR | int | decimal | 0
GLOBAL_TIMER_TIMEOUT_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 33 | GLOBAL_TIMER_TIMEOUT_ERROR | int | decimal | 0
CORROSION_PROBE_1_RTD_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 48 | CORROSION_PROBE_1_RTD_ERROR | int | decimal | 0
CORROSION_PROBE_1_EEPROM_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 50 | CORROSION_PROBE_1_EEPROM_ERROR | int | decimal | 0
CORROSION_PROBE_1_CENTERING_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 51 | CORROSION_PROBE_1_CENTERING_ERROR | int | decimal | 0
CORROSION_PROBE_1_20MV_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 52 | CORROSION_PROBE_1_20MV_ERROR | int | decimal | 0
CORROSION_PROBE_2_RTD_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 57 | CORROSION_PROBE_2_RTD_ERROR | int | decimal | 0
CORROSION_PROBE_2_EEPROM_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 59 | CORROSION_PROBE_2_EEPROM_ERROR | int | decimal | 0
CORROSION_PROBE_2_CENTERING_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 60 | CORROSION_PROBE_2_CENTERING_ERROR | int | decimal | 0
CORROSION_PROBE_2_20MV_ERROR | 1 | 1 | 1000 | DISCRETE_INPUTS | NO | 61 | CORROSION_PROBE_2_20MV_ERROR | int | decimal | 0
COUNTER_1 | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 30 | COUNTER_VALUE_1 | long int | decimal | 1234
COUNTER_2 | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 32 | COUNTER_VALUE_2 | long int | decimal | 1234
GLOBAL_TIMEOUT_VALUE_LEFT | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 34 | GLOBAL_TIMEOUT_VALUE_LEFT | float | decimal | 214758.2
CORROSION_PROBE_1_K_FACTOR | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 52 | CORROSION_PROBE_1_K_FACTOR_VALUE | float | decimal | 214758.2
CORROSION_PROBE_2_K_FACTOR | 1 | 1 | 1000 | INPUT_REGISTERS | NO | 54 | CORROSION_PROBE_2_K_FACTOR_VALUE | int | decimal | 1234
PROBE_1_MFG_SERIAL_NUMBER | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 56 | PROBE_1_MFG_SERIAL_NUMBER_VALUE | long int | decimal | 1234
PROBE_1_MFG_DATE | 1 | 1 | 1000 | INPUT_REGISTERS | NO | 58 | PROBE_1_MFG_DATE_VALUE | int | decimal | 1234
PROBE_2_MFG_SERIAL_NUMBER | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 59 | PROBE_2_MFG_SERIAL_NUMBER_VALUE | long int | decimal | 1234
PROBE_2_MFG_DATE | 1 | 1 | 1000 | INPUT_REGISTERS | NO | 61 | PROBE_2_MFG_DATE_VALUE | int | decimal | 1234
PROBE_1_SENSOR_TYPE | 1 | 1 | 1000 | INPUT_REGISTERS | NO | 62 | PROBE_1_SENSOR_TYPE | int | decimal | 1234
PROBE_2_SENSOR_TYPE | 1 | 1 | 1000 | INPUT_REGISTERS | NO | 63 | PROBE_2_SENSOR_TYPE | int | decimal | 1234
SENSOR_BOARD_FIRMWARE_VERSION | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 64 | SENSOR_BOARD_FIRMWARE_VERSION | float | decimal | 214758.2
CORROSION_BOARD_FIRMWARE_VERSION | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 66 | CORROSION_BOARD_FIRMWARE_VERSION | float | decimal | 214758.2
PH_CAL_SOLUTION_1_VALUE | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 68 | PH_CAL_SOLUTION_1_VALUE | float | decimal | 7
PH_CAL_SOLUTION_2_VALUE | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 70 | PH_CAL_SOLUTION_2_VALUE | float | decimal | 10
ORP_STEP_1_VALUE | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 72 | ORP_STEP_1_VALUE | float | decimal | 1000
ORP_STEP_2_VALUE | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 74 | ORP_STEP_2_VALUE | float | decimal | -1000
ELEC_CONDUCTIVITY_STEP_1_VALUE | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 76 | ELEC_CONDUCTIVITY_STEP_1_VALUE | float | decimal | 1413
ELEC_CONDUCTIVITY_STEP_2_VALUE | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 78 | ELEC_CONDUCTIVITY_STEP_2_VALUE | float | decimal | 10000
TOROIDAL_CONDUCTIVITY_STEP_1_VALUE | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 80 | TOROIDAL_CONDUCTIVITY_STEP_1_VALUE | float | decimal | 1413
TOROIDAL_CONDUCTIVITY_STEP_2_VALUE | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 82 | TOROIDAL_CONDUCTIVITY_STEP_2_VALUE | float | decimal | 10000
TOROIDAL_MAX_ADC | 1 | 1 | 1000 | INPUT_REGISTERS | NO | 84 | TOROIDAL_MAX_ADC | int | decimal | 0
TOROIDAL_MIN_ADC | 1 | 1 | 1000 | INPUT_REGISTERS | NO | 85 | TOROIDAL_MAX_ADC | int | decimal | 0
SPARE_IR_ADDRESS_1 | 1 | 1 | 1000 | INPUT_REGISTERS | NO | 86 | SPARE_IR_ADDRESS_1 | int | decimal | 0
SPARE_IR_ADDRESS_2 | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 87 | SPARE_IR_ADDRESS_2 | float | decimal | 10000
SPARE_IR_ADDRESS_3 | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 89 | SPARE_IR_ADDRESS_3 | float | decimal | 10000
SPARE_IR_ADDRESS_4 | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 91 | SPARE_IR_ADDRESS_4 | float | decimal | 10000
SPARE_IR_ADDRESS_5 | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 93 | SPARE_IR_ADDRESS_5 | float | decimal | 10000
SPARE_IR_ADDRESS_6 | 1 | 2 | 1000 | INPUT_REGISTERS | NO | 95 | SPARE_IR_ADDRESS_6 | float | decimal | 10000
ANALOG_INPUT_1_MAX_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 0 | ANALOG_INPUT_1_MAX_ENGINEERING_UNITS | float | decimal | 100
ANALOG_INPUT_1_MIN_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 2 | ANALOG_INPUT_1_MIN_ENGINEERING_UNITS | float | decimal | 0
ANALOG_INPUT_2_MAX_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 4 | ANALOG_INPUT_2_MAX_ENGINEERING_UNITS | float | decimal | 100
ANALOG_INPUT_2_MIN_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 6 | ANALOG_INPUT_2_MIN_ENGINEERING_UNITS | float | decimal | 0
ANALOG_INPUT_3_MAX_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 8 | ANALOG_INPUT_3_MAX_ENGINEERING_UNITS | float | decimal | 100
ANALOG_INPUT_3_MIN_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 10 | ANALOG_INPUT_3_MIN_ENGINEERING_UNITS | float | decimal | 0
ANALOG_INPUT_4_MAX_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 12 | ANALOG_INPUT_4_MAX_ENGINEERING_UNITS | float | decimal | 100
ANALOG_INPUT_4_MIN_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 14 | ANALOG_INPUT_4_MIN_ENGINEERING_UNITS | float | decimal | 0
ANALOG_OUTPUT_1_MAX_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 16 | ANALOG_OUTPUT_1_MAX_ENGINEERING_UNITS | float | decimal | 100
ANALOG_OUTPUT_1_MIN_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 18 | ANALOG_OUTPUT_1_MIN_ENGINEERING_UNITS | float | decimal | 0
ANALOG_OUTPUT_2_MAX_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 20 | ANALOG_OUTPUT_2_MAX_ENGINEERING_UNITS | float | decimal | 100
ANALOG_OUTPUT_2_MIN_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 22 | ANALOG_OUTPUT_2_MIN_ENGINEERING_UNITS | float | decimal | 0
RTD_GENERIC_OFFSET | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 24 | RTD_GENERIC_OFFSET | float | decimal | 0
RTD_CORROSION_OFFSET | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 26 | RTD_CORROSION_OFFSET | float | decimal | 0
RTD_TOROIDAL_OFFSET | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 28 | RTD_TOROIDAL_OFFSET | float | decimal | 0
PH_OFFSET | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 30 | PH_OFFSET | float | decimal | 0
ORP_OFFSET | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 32 | ORP_OFFSET | float | decimal | 0
ELECTRICAL_CONDUCTIVITY_OFFSET | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 34 | ELECTRICAL_CONDUCTIVITY_OFFSET | float | decimal | 0
TOROIDAL_OFFSET | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 36 | TOROIDAL_OFFSET | float | decimal | 0
ELECTRICAL_CONDUCTIVITY_ TEMP_CHANGE_CONSTANT | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 38 | ELECTRICAL_CONDUCTIVITY_ TEMP_CHANGE_CONSTANT | float | decimal | 35.42
TOROIDAL_CONDUCTIVITY_ TEMP_CHANGE_CONSTANT | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 40 | TOROIDAL_CONDUCTIVITY_ TEMP_CHANGE_CONSTANT | float | decimal | 35.42
ANALOG_OUTPUT_1_SET_VALUE_IN_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 42 | ANALOG_OUTPUT_1_SET_VALUE_IN_ENGINEERING_UNITS | float | decimal | 0
ANALOG_OUTPUT_2_SET_VALUE_IN_ENGINEERING_UNITS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 44 | ANALOG_OUTPUT_2_SET_VALUE_IN_ENGINEERING_UNITS | float | decimal | 0
CONDUCTIVITY_MAX_SWITCH_POINT_VALUE | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 46 | CONDUCTIVITY_MAX_SWITCH_POINT_VALUE | float | decimal | 0
CONDUCTIVITY_MIN_SWITCH_POINT_VALUE | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 48 | CONDUCTIVITY_MIN_SWITCH_POINT_VALUE | float | decimal | 0
TOROIDAL_MAX_SWITCH_POINT_VALUE | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 50 | TOROIDAL_MAX_SWITCH_POINT_VALUE | float | decimal | 0
TOROIDAL_MIN_SWITCH_POINT_VALUE | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 52 | TOROIDAL_MIN_SWITCH_POINT_VALUE | float | decimal | 0
PH_TEMPRATURE_CHANGE_CONSTANT | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 54 | PH_TEMPRATURE_CHANGE_CONSTANT | float | decimal | 0.19
ORP_TEMPRATURE_CHANGE_CONSTANT | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 56 | ORP_TEMPRATURE_CHANGE_CONSTANT | float | decimal | 0
CALIBRATION_GLOBAL_TIMEOUT_SEC | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 58 | CALIBRATION_GLOBAL_TIMEOUT_SEC | float | decimal | 12000
CALIBRATION_GLOBAL_DELAY_SEC | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 60 | CALIBRATION_GLOBAL_DELAY_SEC | float | decimal | 2
PH_MAX_TIME_TO_RUN_CALIBRATION_STEP_SEC | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 62 | PH_MAX_TIME_TO_RUN_CALIBRATION_STEP_SEC | float | decimal | 20
PH_MINDELTA_TO_CONSIDER_DONE | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 64 | PH_MINDELTA_TO_CONSIDER_DONE | float | decimal | 0.1
ORP_MAX_TIME_TO_RUN_CALIBRATION_STEP_SEC | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 66 | ORP_MAX_TIME_TO_RUN_CALIBRATION_STEP_SEC | float | decimal | 20
ORP_MINDELTA_TO_CONSIDER_DONE_MILLIVOLTS | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 68 | ORP_MINDELTA_TO_CONSIDER_DONE_MILLIVOLTS | float | decimal | 50
CONDUCTIVITY_MAX_TIME_TO_RUN_CALIBRATION_STEP_SEC | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 70 | CONDUCTIVITY_MAX_TIME_TO_RUN_CALIBRATION_STEP_SEC | float | decimal | 20
CONDUCTIVITY_MINDELTA_TO_CONSIDER_DONE_MICROSIM | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 72 | CONDUCTIVITY_MINDELTA_TO_CONSIDER_DONE_MICROSIM | float | decimal | 50
TOROIDAL_CONDUCTIVITY_MAX_TIME_TO_RUN_CALIBRATION_STEP_SEC | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 74 | TOROIDAL_CONDUCTIVITY_MAX_TIME_TO_RUN_CALIBRATION_STEP_SEC | float | decimal | 20
TOROIDAL_CONDUCTIVITY_MINDELTA_TO_CONSIDER_DONE_MICROSIM | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 76 | TOROIDAL_CONDUCTIVITY_MINDELTA_TO_CONSIDER_DONE_MICROSIM | float | decimal | 50
SPARE_HR_ADDRESS_1 | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 78 | SPARE_HR_ADDRESS_1 | float | decimal | 50
SPARE_HR_ADDRESS_2 | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 80 | SPARE_HR_ADDRESS_2 | float | decimal | 50
SPARE_HR_ADDRESS_3 | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 82 | SPARE_HR_ADDRESS_3 | float | decimal | 50
SPARE_HR_ADDRESS_4 | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 84 | SPARE_HR_ADDRESS_4 | float | decimal | 50
SPARE_HR_ADDRESS_5 | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 86 | SPARE_HR_ADDRESS_5 | float | decimal | 50
COMMAND_REGISTER | 1 | 1 | 1000 | HOLDING_REGISTERS | NO | 88 | COMMAND_REGISTER | int | decimal | 1
PARAMETER_1_REGISTER | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 89 | PARAMETER_1_REGISTER | float | decimal | 1234
PARAMETER_2_REGISTER | 1 | 2 | 1000 | HOLDING_REGISTERS | NO | 91 | PARAMETER_2_REGISTER | float | decimal | 1234
RESPONSE_REGISTER | 1 | 1 | 1000 | HOLDING_REGISTERS | NO | 93 | RESPONSE_REGISTER | int | decimal | 0